{"text_format":"3","workbook":"xlsx","n_sheets":2,"sheets":["消防返修","Sheet1"],"read":"whole","date_system":"1900"}

{"sheet":"消防返修","index":0,"n_rows":43,"n_cols":8,"rows_kept":43,"merged":[[0,0,0,7],[38,1,38,5],[38,6,38,7],[39,0,39,7]]}
["绿港·云海湾南区消防设施质保期内质量问题整改工程量清单"]
["序号","楼栋","质量问题整改内容","单位","数量\n","单价\n（元）","合价（元）","备注"]
[1,"地下室","六分区消防拉力杆打穿应急照明线管","米",250,null,null,"需更换电线，重新敷设明管"]
[2,"地下室","消防喷淋2泵启动故障","项",1,null,null,"检查，维修"]
[3,"9栋地下室","1个烟感故障","个",1,null,null,"更换烟感"]
[4,"地下室","5分区10个声光故障","项",1,null,null,"检查，维修"]
[5,"地下室","7分区3个烟感故障","个",3,null,null,"更换设备"]
[6,"消控室","消防电话故障","台",1,null,null,"检查，维修，更换分机"]
[7,"消控室","主机线路故障","项",1,null,null,"检查及更换线路"]
[8,"三分区","排风风机电箱故障","台",1,null,null,"更换原器件"]
[9,"6栋14层","电气火灾监控设备故障","台",1,null,null,"更换互感器"]
[10,"楼栋","防火门监控器故障","项",1,null,null,"检查，维修"]
[11,"6栋二单元","多线故障","台",1,null,null,"检查线路，更换模快"]
[12,"三分区","低压风机不启动","台",1,null,null,"检查原器件，更换"]
[13,"4/5分区","卷帘门破损","项",2,null,null,"检查，维修"]
[14,"四分区","烟感故障","个",1,null,null,"更换烟感"]
[15,"8栋二单元6层","烟感故障","个",1,null,null,"更换烟感"]
[16,"消防水池房","风机高压不启动","台",1,null,null,"检查原器件，维修"]
[17,"5栋楼顶","风机高低不启动","台",1,null,null,"检查原器件，维修"]
[18,"二分区","风机不启动","台",1,null,null,"检查原器件，维修"]
[19,"1栋","高位水箱探头失效","台",1,null,null,"更换传感器"]
[20,"6栋二单元","送风机故障","台",1,null,null,"检查原器件，维修"]
[21,"五分区","烟感故障","个",1,null,null,"更换烟感"]
[22,"6栋1单元三层","手报故障","个",1,null,null,"更换设备"]
[23,"二分区","变电非消故障","个",1,null,null,"更换模块"]
[24,"8栋一单元楼顶","防火阀损坏","项",1,null,null,"检查，维修"]
[25,"8栋一单元13层","烟感故障","个",1,null,null,"更换烟感"]
[26,"5栋","消防广播失效","项",1,null,null,"检查线路，更换模块及维修"]
[27,"3、5、6、8栋","应急照明灯故障118个","个",118,null,null,"检查线路，更换设备"]
[28,"3栋","疏散指示灯故障2个","个",2,null,null,"更换设备"]
[29,"地下室","消防喷淋2泵启动故障，一分区应急照明灯故障10个；二分区发电机储油间放气灯故障，应急照明灯故障6个；三分区应急照明灯故障5个；四分区应急照明灯故障25个，疏散指示灯故障2个；五分区应急照明灯故障12个，疏散指示灯故障3个，六分区应急照明灯故障5个，疏散指示灯故障5个，安全出口指示牌故障1个；应急照明灯故障6个，疏散指示灯故障3个，人防处1扇防火门损坏。","项",1,null,null,"检查，维修，更换设备"]
[30,"地下室","五分区三个声光故障","项",1,null,null,"更换设备及检查线路"]
[31,"地下室","5分区10个声光故障","项",1,null,null,"更换设备及检查线路"]
[32,"地下室","7分区3个烟感故障","个",3,null,null,"更换设备"]
[33,"消控室","二分区接地故障","项",1,null,null,"检查，维修"]
[34,"1栋10层1010号房","烟感故障","个",1,null,null,"更换烟感"]
[35,"消控室","消防电源监测控制器回路故障","项",1,null,null,"检查线路，更换线路"]
[36,"16栋101（后面）","室外消火栓漏水","处",1,null,null,"检查，维修"]
[37,"合计（元）"]
["说明：1、报价包含了人工费、材料费、机械费、设备费、加班费、夜间施工增加费、二次搬运费、水电费、现场垃圾清运费、成品保护费、因拆旧而损坏其它物件的修复、更换费、安全文明施工费、高空作业费、管理费、利润、税金等为实现本工程目的的一切费用，总价包干。\n2、请单内的项目、数量为暂列，成交人进场后需重新排查，如有新增的维修整改，成交人须完成整改维修，整改维修的费用包含在本报价内，采购人不予另外支付。"]
[null,null,"报价单位（盖章）："]
[null,null,"法定代表人或委托代理人："]
[null,null,"日期："]

{"sheet":"Sheet1","index":1,"n_rows":0,"n_cols":0,"rows_kept":0}